## Resumen
Caso | Barra_Falla | Tipo_Falla | Valido | Detalle
CasoBase | P1 15302 13.2kV | Trifasico | TRUE | m:Ikss
CasoBase | P1 15302 13.2kV | Bifasico | TRUE | m:Ikss:B
CasoBase | P1 15302 13.2kV | Monofasico | TRUE | m:Ikss
CasoBase | P1 15303 13.2kV | Trifasico | TRUE | m:Ikss
CasoBase | P1 15303 13.2kV | Bifasico | TRUE | m:Ikss:B
CasoBase | P1 15303 13.2kV | Monofasico | TRUE | m:Ikss
CasoBase | P1 15340 13.2kV | Trifasico | TRUE | m:Ikss
CasoBase | P1 15340 13.2kV | Bifasico | TRUE | m:Ikss:B
CasoBase | P1 15340 13.2kV | Monofasico | TRUE | m:Ikss
CasoBase | P1 15344 13.2kV | Trifasico | TRUE | m:Ikss
CasoBase | P1 15344 13.2kV | Bifasico | TRUE | m:Ikss:B
CasoBase | P1 15344 13.2kV | Monofasico | TRUE | m:Ikss
CasoBase | P2 15302 13.2kV | Trifasico | TRUE | m:Ikss
CasoBase | P2 15302 13.2kV | Bifasico | TRUE | m:Ikss:B
CasoBase | P2 15302 13.2kV | Monofasico | TRUE | m:Ikss
CasoBase | P2 15303 13.2kV | Trifasico | TRUE | m:Ikss
CasoBase | P2 15303 13.2kV | Bifasico | TRUE | m:Ikss:B
CasoBase | P2 15303 13.2kV | Monofasico | TRUE | m:Ikss
CasoBase | P2 15340 13.2kV | Trifasico | TRUE | m:Ikss
CasoBase | P2 15340 13.2kV | Bifasico | TRUE | m:Ikss:B
CasoBase | P2 15340 13.2kV | Monofasico | TRUE | m:Ikss
CasoBase | P2 15344 13.2kV | Trifasico | TRUE | m:Ikss
CasoBase | P2 15344 13.2kV | Bifasico | TRUE | m:Ikss:B
CasoBase | P2 15344 13.2kV | Monofasico | TRUE | m:Ikss
CasoBase | P3 15344 13.2kV | Trifasico | TRUE | m:Ikss
CasoBase | P3 15344 13.2kV | Bifasico | TRUE | m:Ikss:B
CasoBase | P3 15344 13.2kV | Monofasico | TRUE | m:Ikss
CasoBase | P4 153344 13.2kV | Trifasico | TRUE | m:Ikss
CasoBase | P4 153344 13.2kV | Bifasico | TRUE | m:Ikss:B
CasoBase | P4 153344 13.2kV | Monofasico | TRUE | m:Ikss
CasoBase | P5 15344 13.2kV | Trifasico | TRUE | m:Ikss
CasoBase | P5 15344 13.2kV | Bifasico | TRUE | m:Ikss:B
CasoBase | P5 15344 13.2kV | Monofasico | TRUE | m:Ikss
CasoBase | P6 15344 13.2kV | Trifasico | TRUE | m:Ikss
CasoBase | P6 15344 13.2kV | Bifasico | TRUE | m:Ikss:B
CasoBase | P6 15344 13.2kV | Monofasico | TRUE | m:Ikss
CasoBase | PTO BOYACA 13.2kV | Trifasico | TRUE | m:Ikss
CasoBase | PTO BOYACA 13.2kV | Bifasico | TRUE | m:Ikss:B
CasoBase | PTO BOYACA 13.2kV | Monofasico | TRUE | m:Ikss
CasoBase | PTO BOYACA 34.5kV | Trifasico | TRUE | m:Ikss
CasoBase | PTO BOYACA 34.5kV | Bifasico | TRUE | m:Ikss:B
CasoBase | PTO BOYACA 34.5kV | Monofasico | TRUE | m:Ikss
CasoBase | PTO BOYACA HV 115 | Trifasico | TRUE | m:Ikss
CasoBase | PTO BOYACA HV 115 | Bifasico | TRUE | m:Ikss:B
CasoBase | PTO BOYACA HV 115 | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | TRUE | m:Ikss
GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | TRUE | m:Ikss:B
GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | TRUE | m:Ikss

## Variations_Faltantes
Network_Variation_no_encontrada_en_PowerFactory

## Nodos
Nombre | Caso | Barra_Falla | Tipo_Falla | Ikss_kA | Skss_MVA | Atributo_leido
P1 15302 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 4.2595 | 97385.6017 | m:Ikss
P1 15302 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 3.6888 | 28112.8017 | m:Ikss:B
P1 15302 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 4.2595 | 32461.8673 | m:Ikss
P1 15303 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 5.2082 | 119075.8744 | m:Ikss
P1 15303 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 4.5104 | 34374.2442 | m:Ikss:B
P1 15303 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 5.2082 | 39691.9582 | m:Ikss
P1 15340 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 6.6782 | 152684.234 | m:Ikss
P1 15340 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 5.7835 | 44076.1421 | m:Ikss:B
P1 15340 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 6.6782 | 50894.7449 | m:Ikss
P1 15344 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 4.112 | 94013.8766 | m:Ikss
P1 15344 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 3.5611 | 27139.4692 | m:Ikss:B
P1 15344 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 4.112 | 31337.9594 | m:Ikss
P2 15302 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 1.5263 | 34895.9878 | m:Ikss
P2 15302 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 1.3218 | 10073.604 | m:Ikss:B
P2 15302 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 1.5263 | 11631.9959 | m:Ikss
P2 15303 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 2.18 | 49842.1757 | m:Ikss
P2 15303 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 1.888 | 14388.1968 | m:Ikss:B
P2 15303 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 2.18 | 16614.0586 | m:Ikss
P2 15340 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 3.8909 | 88958.0131 | m:Ikss
P2 15340 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 3.3696 | 25679.9665 | m:Ikss:B
P2 15340 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 3.8909 | 29652.6711 | m:Ikss
P2 15344 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 1.8559 | 42432.6983 | m:Ikss
P2 15344 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 1.6073 | 12249.2656 | m:Ikss:B
P2 15344 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 1.8559 | 14144.2333 | m:Ikss
P3 15344 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 1.2357 | 28252.7581 | m:Ikss
P3 15344 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 1.0702 | 8155.8695 | m:Ikss:B
P3 15344 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 1.2357 | 9417.5866 | m:Ikss
P4 153344 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0.77027 | 17610.6379 | m:Ikss
P4 153344 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0.66707 | 5083.754 | m:Ikss:B
P4 153344 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0.77027 | 5870.2132 | m:Ikss
P5 15344 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0.76429 | 17474.0223 | m:Ikss
P5 15344 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0.66189 | 5044.3165 | m:Ikss:B
P5 15344 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0.76429 | 5824.6746 | m:Ikss
P6 15344 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0.32872 | 7515.4758 | m:Ikss
P6 15344 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0.28468 | 2169.5314 | m:Ikss:B
P6 15344 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0.32872 | 2505.1589 | m:Ikss
PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 8.121 | 185670.5922 | m:Ikss
PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 7.033 | 53598.4837 | m:Ikss:B
PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 8.121 | 61890.1978 | m:Ikss
PTO BOYACA 34.5kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 2.0094 | 120075.2893 | m:Ikss
PTO BOYACA 34.5kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 1.7402 | 34662.7505 | m:Ikss:B
PTO BOYACA 34.5kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 2.0094 | 40025.0966 | m:Ikss
PTO BOYACA HV 115 | CasoBase | PTO BOYACA HV 115 | Trifasico | 6.002 | 1195513.4955 | m:Ikss
PTO BOYACA HV 115 | CasoBase | PTO BOYACA HV 115 | Bifasico | 5.1979 | 345115.0198 | m:Ikss:B
PTO BOYACA HV 115 | CasoBase | PTO BOYACA HV 115 | Monofasico | 6.002 | 398504.499 | m:Ikss
P1 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 4.2822 | 97904.9578 | m:Ikss
P1 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 3.6888 | 28112.8025 | m:Ikss:B
P1 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 4.2603 | 32467.8192 | m:Ikss
P1 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 5.236 | 119710.9044 | m:Ikss
P1 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 4.5105 | 34374.2458 | m:Ikss:B
P1 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 5.2095 | 39701.4055 | m:Ikss
P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 6.7138 | 153498.497 | m:Ikss
P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 5.7835 | 44076.1461 | m:Ikss:B
P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 6.6804 | 50911.3526 | m:Ikss
P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 4.1553 | 95004.0555 | m:Ikss
P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 3.5611 | 27139.4801 | m:Ikss:B
P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 4.1148 | 31358.9999 | m:Ikss
P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 1.5344 | 35082.0877 | m:Ikss
P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 1.3218 | 10073.604 | m:Ikss:B
P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 1.5264 | 11632.5902 | m:Ikss
P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 2.1917 | 50107.9834 | m:Ikss
P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 1.888 | 14388.1968 | m:Ikss:B
P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 2.1802 | 16615.3621 | m:Ikss
P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 3.9117 | 89432.4251 | m:Ikss
P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 3.3696 | 25679.967 | m:Ikss:B
P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 3.8915 | 29657.5064 | m:Ikss
P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 1.8755 | 42879.6106 | m:Ikss
P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 1.6073 | 12249.2677 | m:Ikss:B
P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 1.8566 | 14149.0839 | m:Ikss
P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 1.2488 | 28550.3236 | m:Ikss
P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 1.0702 | 8155.8704 | m:Ikss:B
P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 1.236 | 9419.7812 | m:Ikss
P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0.77838 | 17796.1178 | m:Ikss
P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0.66707 | 5083.7543 | m:Ikss:B
P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0.77038 | 5871.0763 | m:Ikss
P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0.77234 | 17658.0632 | m:Ikss
P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0.66189 | 5044.3168 | m:Ikss:B
P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0.7644 | 5825.5245 | m:Ikss
P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0.33218 | 7594.6308 | m:Ikss
P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0.28468 | 2169.5315 | m:Ikss:B
P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0.32874 | 2505.3176 | m:Ikss
PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 8.1643 | 186660.7711 | m:Ikss
PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 7.033 | 53598.4917 | m:Ikss:B
PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 8.1243 | 61915.4052 | m:Ikss
PTO BOYACA 34.5kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 2.0205 | 120737.5784 | m:Ikss
PTO BOYACA 34.5kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 1.7402 | 34662.7541 | m:Ikss:B
PTO BOYACA 34.5kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 2.01 | 40036.3714 | m:Ikss
PTO BOYACA HV 115 | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 6.007 | 1196503.6744 | m:Ikss
PTO BOYACA HV 115 | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 5.1979 | 345115.0284 | m:Ikss:B
PTO BOYACA HV 115 | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 6.0024 | 398529.5789 | m:Ikss
Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 14.1641 | 19626.3376 | m:Ikss
Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 11.6476 | 5379.804 | m:Ikss:B
Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 13.4932 | 6232.2328 | m:Ikss

## Lineas
Nombre | Nodo_I | Nodo_J | Caso | Barra_Falla | Tipo_Falla | Ikss_bus1_kA | Ikss_bus2_kA
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 4.2595 | 4.2595
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 4.2595 | 4.2595
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 5.2082 | 5.2082
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 5.2082 | 5.2082
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 6.6782 | 6.6782
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 6.6782 | 6.6782
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 4.112 | 4.112
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 4.112 | 4.112
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 1.5263 | 1.5263
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 1.5263 | 1.5263
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 1.5263 | 1.5263
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 1.5263 | 1.5263
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 2.18 | 2.18
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 2.18 | 2.18
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 2.18 | 2.18
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 2.18 | 2.18
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 3.8909 | 3.8909
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 3.8909 | 3.8909
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 3.8909 | 3.8909
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 3.8909 | 3.8909
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 1.8559 | 1.8559
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 1.8559 | 1.8559
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 1.8559 | 1.8559
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 1.8559 | 1.8559
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 1.2357 | 1.2357
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 1.2357 | 1.2357
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 1.2357 | 1.2357
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 1.2357 | 1.2357
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 1.2357 | 1.2357
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 1.2357 | 1.2357
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0.77027 | 0.77027
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0.77027 | 0.77027
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0.77027 | 0.77027
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0.77027 | 0.77027
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0.77027 | 0.77027
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0.77027 | 0.77027
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0.77027 | 0.77027
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0.77027 | 0.77027
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0.76429 | 0.76429
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0.76429 | 0.76429
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0.76429 | 0.76429
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0.76429 | 0.76429
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0.76429 | 0.76429
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0.76429 | 0.76429
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0.76429 | 0.76429
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0.76429 | 0.76429
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0.76429 | 0.76429
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0.76429 | 0.76429
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0.32872 | 0.32872
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0.32872 | 0.32872
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0.32872 | 0.32872
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0.32872 | 0.32872
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0.32872 | 0.32872
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0.32872 | 0.32872
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0.32872 | 0.32872
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0.32872 | 0.32872
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0.32872 | 0.32872
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0.32872 | 0.32872
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0.32872 | 0.32872
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0.32872 | 0.32872
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 4.2822 | 4.2822
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0.043309 | 0.043309
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 4.2603 | 4.2603
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0.0017347 | 0.0017347
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0.043309 | 0.043309
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 5.236 | 5.236
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 1.1521e-06 | 1.1521e-06
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0.0021211 | 0.0021211
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 5.2095 | 5.2095
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0.043309 | 0.043309
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 6.7138 | 6.7138
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 1.4773e-06 | 1.4773e-06
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0.0027201 | 0.0027201
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 6.6804 | 6.6804
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 4.112 | 4.112
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 1.7965e-06 | 1.7965e-06
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 4.112 | 4.112
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 1.5344 | 1.5344
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0.043309 | 0.043309
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 1.5344 | 1.5344
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 1.5264 | 1.5264
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0.0006215 | 0.0006215
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 1.5264 | 1.5264
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0.043309 | 0.043309
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 2.1917 | 2.1917
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 2.1917 | 2.1917
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0.00088771 | 0.00088771
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 2.1802 | 2.1802
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 2.1802 | 2.1802
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0.043309 | 0.043309
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 3.9117 | 3.9117
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 3.9117 | 3.9117
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0.0015845 | 0.0015845
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 3.8915 | 3.8915
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 3.8915 | 3.8915
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 1.8336 | 1.8336
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 1.8755 | 1.8755
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 1.8553 | 1.8553
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 1.8566 | 1.8566
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 1.2076 | 1.2076
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 1.2488 | 1.2488
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 1.2488 | 1.2488
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 1.2352 | 1.2352
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 1.236 | 1.236
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 1.236 | 1.236
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0.73806 | 0.73806
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0.77838 | 0.77838
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0.77838 | 0.77838
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0.77838 | 0.77838
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0.76986 | 0.76986
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0.77038 | 0.77038
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0.77038 | 0.77038
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0.77038 | 0.77038
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0.77234 | 0.77234
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0.73204 | 0.73204
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0.77234 | 0.77234
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0.77234 | 0.77234
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0.77234 | 0.77234
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0.7644 | 0.7644
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0.76389 | 0.76389
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0.7644 | 0.7644
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0.7644 | 0.7644
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0.7644 | 0.7644
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0.33218 | 0.33218
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0.29297 | 0.29297
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0.33218 | 0.33218
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0.33218 | 0.33218
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0.33218 | 0.33218
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0.33218 | 0.33218
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0 | 0
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0.32874 | 0.32874
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0.32852 | 0.32852
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0.32874 | 0.32874
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0.32874 | 0.32874
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0.32874 | 0.32874
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0.32874 | 0.32874
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0.043309 | 0.043309
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 1.7965e-06 | 1.7965e-06
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0.003308 | 0.003308
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0.043309 | 0.043309
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 1.2016e-06 | 1.2016e-06
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0.0022123 | 0.0022123
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0.043309 | 0.043309
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 1.7965e-06 | 1.7965e-06
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0.0033068 | 0.0033068
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0.81512 | 0.81512
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 1.6275e-06 | 1.6275e-06
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0 | 0
AL 0.087km | P4 153344 13.2kV | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0 | 0
AL 1.24km | P1 15302 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0 | 0
AL 1.32km | PTO BOYACA 13.2kV | P1 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0.81488 | 0.81488
AL 2.34km | P2 15344 13.2kV | P3 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0 | 0
AL 2.64km | P1 15344 13.2kV | P2 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0 | 0
AL 4.2km | P3 15344 13.2kV | P4 153344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0 | 0
Al 0.36km | PTO BOYACA 13.2kV | P1 15340 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0 | 0
Al 0.82km | P1 15303 13.2kV | PTO BOYACA 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0 | 0
Al 1.09km | P1 15340 13.2kV | P2 15340 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0 | 0
Al 14.833km | P5 15344 13.2kV | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0 | 0
Al 2.44km | P1 15303 13.2kV | P2 15303 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0 | 0
Al 3.73km | P1 15302 13.2kV | P2 15302 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0 | 0

## Transformadores_2Devanados
Nombre | Caso | Barra_Falla | Tipo_Falla | Ikss_HV_kA | Ikss_LV_kA
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0 | 1.4576e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0.0017346 | 9.7221e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 1.0801e-06 | 1.7822e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0.0021211 | 1.1888e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 1.385e-06 | 2.2852e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0.00272 | 1.5245e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 1.6842e-06 | 2.7789e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0.0033088 | 1.8545e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0 | 5.2228e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0.00062149 | 3.4832e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0 | 7.4598e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0.0008877 | 4.9753e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0 | 1.3314e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0.0015845 | 8.8806e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0 | 1.2542e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0.0014929 | 8.3673e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0 | 8.3511e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0.00099391 | 5.5705e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0 | 5.2054e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0.00061948 | 3.472e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0 | 5.1651e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0.00061467 | 3.445e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0 | 2.2215e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0.00026434 | 1.4816e-06
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 1.6842e-06 | 2.7789e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0.0033079 | 1.854e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 1.1265e-06 | 1.8587e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0.0022123 | 1.2399e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0.043309 | 0.7146
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 1.6842e-06 | 2.7789e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0.0033068 | 1.8533e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0.81512 | 13.4495
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 1.6076e-06 | 2.6526e-05
Tr puerto Boyaca 1.25MW | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0.81488 | 13.4932

## Transformadores_3Devanados
Nombre | Caso | Barra_Falla | Tipo_Falla | Ikss_HV_kA | Ikss_MV_kA | Ikss_LV_kA
3-Winding Transformer | CasoBase | P1 15302 13.2kV | Trifasico | 0.48892 | 0 | 4.2595
3-Winding Transformer | CasoBase | P1 15302 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | P1 15302 13.2kV | Monofasico | 0.48892 | 0 | 4.2595
3-Winding Transformer | CasoBase | P1 15303 13.2kV | Trifasico | 0.59781 | 0 | 5.2082
3-Winding Transformer | CasoBase | P1 15303 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | P1 15303 13.2kV | Monofasico | 0.59781 | 0 | 5.2082
3-Winding Transformer | CasoBase | P1 15340 13.2kV | Trifasico | 0.76654 | 0 | 6.6782
3-Winding Transformer | CasoBase | P1 15340 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | P1 15340 13.2kV | Monofasico | 0.76654 | 0 | 6.6782
3-Winding Transformer | CasoBase | P1 15344 13.2kV | Trifasico | 0.47199 | 0 | 4.112
3-Winding Transformer | CasoBase | P1 15344 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | P1 15344 13.2kV | Monofasico | 0.47199 | 0 | 4.112
3-Winding Transformer | CasoBase | P2 15302 13.2kV | Trifasico | 0.17519 | 0 | 1.5263
3-Winding Transformer | CasoBase | P2 15302 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | P2 15302 13.2kV | Monofasico | 0.17519 | 0 | 1.5263
3-Winding Transformer | CasoBase | P2 15303 13.2kV | Trifasico | 0.25023 | 0 | 2.18
3-Winding Transformer | CasoBase | P2 15303 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | P2 15303 13.2kV | Monofasico | 0.25023 | 0 | 2.18
3-Winding Transformer | CasoBase | P2 15340 13.2kV | Trifasico | 0.44661 | 0 | 3.8909
3-Winding Transformer | CasoBase | P2 15340 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | P2 15340 13.2kV | Monofasico | 0.44661 | 0 | 3.8909
3-Winding Transformer | CasoBase | P2 15344 13.2kV | Trifasico | 0.21303 | 0 | 1.8559
3-Winding Transformer | CasoBase | P2 15344 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | P2 15344 13.2kV | Monofasico | 0.21303 | 0 | 1.8559
3-Winding Transformer | CasoBase | P3 15344 13.2kV | Trifasico | 0.14184 | 0 | 1.2357
3-Winding Transformer | CasoBase | P3 15344 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | P3 15344 13.2kV | Monofasico | 0.14184 | 0 | 1.2357
3-Winding Transformer | CasoBase | P4 153344 13.2kV | Trifasico | 0.088413 | 0 | 0.77027
3-Winding Transformer | CasoBase | P4 153344 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | P4 153344 13.2kV | Monofasico | 0.088413 | 0 | 0.77027
3-Winding Transformer | CasoBase | P5 15344 13.2kV | Trifasico | 0.087727 | 0 | 0.76429
3-Winding Transformer | CasoBase | P5 15344 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | P5 15344 13.2kV | Monofasico | 0.087727 | 0 | 0.76429
3-Winding Transformer | CasoBase | P6 15344 13.2kV | Trifasico | 0.037731 | 0 | 0.32872
3-Winding Transformer | CasoBase | P6 15344 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | P6 15344 13.2kV | Monofasico | 0.037731 | 0 | 0.32872
3-Winding Transformer | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0.93215 | 0 | 8.121
3-Winding Transformer | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0.93215 | 0 | 8.121
3-Winding Transformer | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0.60283 | 2.0094 | 0
3-Winding Transformer | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0.60283 | 2.0094 | 0
3-Winding Transformer | CasoBase | PTO BOYACA HV 115 | Trifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | PTO BOYACA HV 115 | Bifasico | 0 | 0 | 0
3-Winding Transformer | CasoBase | PTO BOYACA HV 115 | Monofasico | 0 | 0 | 0
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0.4873 | 0 | 4.2454
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0.48881 | 0 | 4.2586
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0.5965 | 0 | 5.1968
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0 | 0 | 1.1521e-06
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0.59771 | 0 | 5.2073
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0.7658 | 0 | 6.6718
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0 | 0 | 1.4773e-06
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0.76648 | 0 | 6.6777
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0.47199 | 0 | 4.112
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0 | 0 | 1.7965e-06
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0.47199 | 0 | 4.112
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0.1729 | 0 | 1.5063
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0.17513 | 0 | 1.5258
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0.24807 | 0 | 2.1612
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0.25015 | 0 | 2.1793
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0.44488 | 0 | 3.8759
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0.4465 | 0 | 3.89
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0.21046 | 0 | 1.8336
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0.21296 | 0 | 1.8553
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0.13862 | 0 | 1.2076
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0.14178 | 0 | 1.2352
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0.084717 | 0 | 0.73806
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0.088367 | 0 | 0.76986
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0.084025 | 0 | 0.73204
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0.087681 | 0 | 0.76389
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0.033628 | 0 | 0.29297
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0 | 0 | 0
3-Winding Transformer | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0.037708 | 0 | 0.32852
3-Winding Transformer | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0.93215 | 0 | 8.121
3-Winding Transformer | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0 | 0 | 1.7965e-06
3-Winding Transformer | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0.93215 | 0 | 8.121
3-Winding Transformer | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0.60118 | 2.0205 | 0.043309
3-Winding Transformer | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0 | 0 | 1.2016e-06
3-Winding Transformer | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0.60275 | 2.01 | 0.0022123
3-Winding Transformer | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0.0049711 | 0 | 0.043309
3-Winding Transformer | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0 | 0 | 1.7965e-06
3-Winding Transformer | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0.00037957 | 0 | 0.0033068
3-Winding Transformer | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0.093562 | 0 | 0.81512
3-Winding Transformer | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0 | 0 | 1.6275e-06
3-Winding Transformer | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0.093534 | 0 | 0.81488

## Generadores
Nombre | Barra | Caso | Barra_Falla | Tipo_Falla | Ikss_kA
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 1.4576e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 9.7188e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 1.7822e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 1.1884e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 2.2852e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 1.524e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 2.7789e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 1.8538e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 5.2228e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 3.4821e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 7.4598e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 4.9736e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 1.3314e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 8.8776e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 1.2542e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 8.3645e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 8.3511e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 5.5687e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 5.2054e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 3.4708e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 5.1651e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 3.4439e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 2.2215e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 1.4811e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 2.7789e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 1.8534e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 1.8587e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 1.2395e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 2.7789e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 1.8527e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 2.6526e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 1.7741e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0

## Generadores_Existentes
Nombre | Barra | Caso | Barra_Falla | Tipo_Falla | Ikss_kA
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15302 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15302 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15302 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15303 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15303 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15303 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15340 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15340 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15340 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15344 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15344 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P1 15344 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15302 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15302 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15302 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15303 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15303 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15303 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15340 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15340 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15340 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15344 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15344 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P2 15344 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P3 15344 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P3 15344 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P3 15344 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P4 153344 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P4 153344 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P4 153344 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P5 15344 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P5 15344 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P5 15344 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P6 15344 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P6 15344 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | P6 15344 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA 13.2kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA 34.5kV | Monofasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Trifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Bifasico | 0
GD P4 15344 | P5 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | CasoBase | PTO BOYACA HV 115 | Monofasico | 0

## Generadores_Con_Proyecto
Nombre | Barra | Caso | Barra_Falla | Tipo_Falla | Ikss_kA
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 1.4576e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 9.7188e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15302 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 1.7822e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 1.1884e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15303 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 2.2852e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 1.524e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15340 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 2.7789e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 1.8538e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P1 15344 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 5.2228e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 3.4821e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15302 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 7.4598e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 4.9736e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15303 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 1.3314e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 8.8776e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15340 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 1.2542e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 8.3645e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P2 15344 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 8.3511e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 5.5687e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P3 15344 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 5.2054e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 3.4708e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P4 153344 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 5.1651e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 3.4439e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P5 15344 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 2.2215e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 1.4811e-06
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | P6 15344 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 2.7789e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 1.8534e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 13.2kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 1.8587e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 1.2395e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA 34.5kV | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 2.7789e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 1.8527e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | PTO BOYACA HV 115 | Monofasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0.7146
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Trifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 2.6526e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Bifasico | 0
Distributed Small PV Plants | Puerto Boyaca 800V | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 1.7741e-05
GD P4 15344 | P5 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0
GD P5 15344 | P6 15344 13.2kV | GD_Puerto_Boyaca_990kW | Puerto Boyaca 800V | Monofasico | 0